# Fixed Testing Intervals

## Frequency of Periodic Inspection & Testing

The frequency of periodic inspection and testing must be determined taking into account:

- the type of installation

- its use and operation

- the frequency and quality of maintenance

- the external influences to which it is subjected

The table below provides guidance on the frequency of formal inspections of electrical installations as well as routine checks.

| Type of Installation | Routine Check | Maximum Period between inspections and testing as necessary | Reference (see notes below) |
| --- | --- | --- | --- |
| General installation |
| Domestic | N/A | change of occupancy/10 years | N/A |
| Commercial | 1 year | change of occupancy/5 years | 1,2 |
| Educational establishments | 4 months | 5 years | 1,2 |
| Hospitals | 1 year | 5 years | 1,2 |
| Industrial | 1 year | 3 years | 1,2 |
| Residential accommodation | at change of occupancy/ 1 year | 5 years | 1 |
| Offices | 1 year | 5 years | 1,2 |
| Shops | 1 year | 5 years | 1,2 |
| Laboratories | 1 year | 5 years | 1,2 |
| Buildings open to the public |
| Cinemas | 4 months | 1 year | 2,6,7 |
| Church installations | 1 year | 5 years | 2 |
| Leisure complexes | 4 months | 1 year | 1,2,6 |
| Places of public entertainment | 1 year | 5 years | 1,2,6 |
| Restaurants and hotels | 4 months | 1 year | 1,2,6 |
| Theatres | 4 months | 1 year | 2,6,7 |
| Public houses | 1 year | 5 years | 1,2,6 |
| Village halls/Community centres | 1 year | 5 years | 1,2 |
| External installations |
| Agricultural and horticultural | 1 year | 3 years | 1,2 |
| Caravans | 1 year | 3 years | N/A |
| Caravan parks | 6 months | 1 year | 1,2,6 |
| Highway power supplies | as convenient | 6 years | N/A |
| Marinas | 4 months | 1 year | 1,2 |
| Fish farms | 4 months | 1 year | 1,2 |
| Emergency lighting | daily/monthly | 3 years | 2,3,4 |
| Fire alarms | daily/weekly/monthly | 1 year | 2,4,5 |
| Laundrettes | 1 year | 1 year | 1,2,6 |
| Petrol filling stations | 1 year | 1 year | 1,2,6 |
| Construction site installations | 3 months | 3 months | 1,2 |

Reference Key

Particular attention must be taken to comply with S1 1988 No 1057.

The Electricity Supply Regulations 1988.

S1 1988 N0 635 The Electricity at Work Regulations.

See BS5266: Part : 1988 Code of practice for the emergency lighting.

Other intervals are recommended for testing operation of batteries and generators.

See BS 5839: Part 1: 1988 Code of practice for system design installation and servicing.

Local Authority Conditions of Licence.

S1 1995 No 1129 (Clause 27) The Cinematography (Safety) Regulations

Information taken from IEE guidance note 3